| **S.No.** | **Item/****Function** | **Potential****Failure Mode****(Failure Mode)** | **Potential Effect of****Failure****(Effect)** | **Potential Cause/****Mechanism of Failure** | **Current Control** | **Reference** | **S** | **O** | **D** | **Risk****Priority****Number****(S\*O\*D)** | **Recommend-ended****Actions****(if any)** | **Post Risk** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **S** | **O** | **D** | **RPN****S\*O\*D** |
| **Entry & Exit With Common Change Rooms:** |
|  | HVAC System  | * Air of three piece line got contaminated with dry powder line air.
 | * There are high chances of cross contamination.
* It can cause product failure.
* Product & Area got contaminated.
 | * Dedicated & Separate Air circulation system not provided.
 | * Separate & dedicated AHU are there for preventing the cross contamination in both areas (Ampoule line-01,Ampoule Line-02 and liquid vial line)
* Due to dedicated AHU for both areas there is no chance of cross contamination in both areas through circulated air.
 | As Per SOP & Validation record | 3 | 1 | 1 | 3Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Differential Pressure  | * Differential Pressure decreases from its set parameters or acceptance limit.
 | * Cross contamination occurs between the adjacent areas.
 | * Low amount of air circulation in area.
* Differential pressure failure and goes out of limit.
* Desired ACPH not getting in area.
* Dumper can be not properly opened.
* Motor & blower do not working properly.

  | * Differential pressure is regularly monitored and controlled through BMS System.
* If the differential pressure goes out of limit then BMS system controls the differential pressure.
 | As Per SOP & Validation record | 3 | 3 | 1 | 9Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Mobile trolley  | * Common mobile trolley is used for transferring the material like machine pasts etc.
 | * Cross contamination occurs between the adjacent areas.
 | * Single trolley is available and in uses for transferring the material to all areas ie.liquid vial, ampoule line-01 & Ampoule line -02.
 | * Saparate and dedicated mobile trolley available for both areas.
 | As Per SOP & Validation record | 4 | 1 | 1 | 20 High risk & adequate recommender action must be required. | * Separate and dedicated mobile trolley available for both areas.
 |  |  |  |  |
|  | Process  | * Bulk solution drop spillage in the area.
 | * Cross contamination occurs
 | * Tank and transfer line not connected properly.
* Manual transfer line is available for transfer the solution.
 | * Integrated product line between manufacturing areas to filtration area to filling area is available for transfer the solution through pneumatic valve which is controlled by PLC.
* Integrated product line available for all areas.
 | As Per SOP & Validation record | 4 | 2 | 1 | 8Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Area monitoring by settle plate & active air sampling | * Irregular monitoring intervals.
* Inadequate detailing of test locations (sample points)
 | * Area monitoring effected and cannot record as per the time schedule.
* Critical locations can be left without monitoring.
 | * No schedule of area monitoring
* No justified and approved locations for area sampling.
* Working personnel lack of adequate knowledge.
 | * The area monitoring has been done as per the schedule for the different area.
* There are proper approved sampling locations for area monitoring.
* Trained personnel done the area monitoring.
 | As Per SOP | 3 | 2 | 1 | 6Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Cleaning & Sanitization | * Area cleaning not done after batch completion.
 | * There is a high degree of chances to increase the chemical & microbial growth in the area that can lead product contamination also.
 | * Unawareness of operator and staff members.
* Working personnel lack of adequate knowledge.
 | * Only trained and authorized per can enter & work in the aseptic area and they all are trained in their work. After completion of every batch the cleaning has been done in the presence of production and quality assurance personnel.
 | As Per SOP | 4 | 1 | 1 | 4Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Area Cleaning  | * Microbial growth increases in aseptic area.
 | * Product get contaminated

 Product failure.  | * Disinfectant using area cleaning not validated.
* Effectiveness of disinfectant not up to the mark.
 | * Disinfectant validation has been done and only validated disinfectant has been used for cleaning of aseptic area.
 | As Per SOP & Validation record | 4 | 2 | 1 | 8Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Area Cleaning | * Area cleaning not done as per the schedule.
 | * High chances to increase the microbial growth in the area that can lead product contamination also.
 | * No schedule is there for area cleaning.
* SOP of area cleaning not followed.
* Working personnel lack of adequate knowledge.
 | * There is a proper schedule for cleaning of aseptic area and cleaning has been done as per the schedule by the trained personnel.
* For cleaning and sanitization only validated & approved disinfectant in use and all validated disinfectants rotated as per scheduled frequency on daily basis.
* For avoiding the cross contamination in all filling rooms (ampoule line 1 & 2 and liquid vial) have been cleaned with a separate lint free MOP and fresh solution.
* all areas clean sequently and never cleaned both areas at a time.
* SOP of area cleaning has been followed and log in the all details in respective log book.
 | As Per SOP | 4 | 2 | 1 | 8Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Material entry in aseptic area | * Material entry not specified
 | * There are high chances of cross contamination.
* It can cause product failure.
 | * Material entry not properly segregated for entering in aseptic area.
 | * There are separate entry procedures for material.
* For ampoule line 01 ,ampoule line-02 and liquid vial line, dynamic pass boxes are available for material entry and there is no chance of cross contamination due to material entry in aseptic area.
* All materials for aseptic area has been transferred through Dynamic pass box.
 | As Per SOP & Validation record | 3 | 1 | 1 | 3Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Man entry in aseptic area  | * Man entry not specified
 | * There are high chances of cross contamination.
* It can cause product failure.
 | * Man entry not properly segregated for entering in aseptic area.
* Entry & exit procedure for aseptic area not specified.
 | * There are three filling room with common entry and exit and a common corridor. So, for preventing the cross contamination dedicated Personnel have been provided for all filling areas.
* All personnel have been enter in the aseptic area through 03 change room system as per the entry & exit procedure for aseptic area.
 | As Per SOP & Validation record | 4 | 2 | 1 | 8Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |
|  | Man entry in aseptic area | * Gowning procedure not defined for entering in aseptic area.
 | * Sterile garments can be reused for second time for aseptic area.
 | * No proper training provided for gowning procedure.
* The procedure is not adequate as per aseptic behavior.
 | * An approved gowning procedure is followed and available in place.
* As per current written procedure reuse of sterile garments is not allowed for entry in aseptic area.
 | As Per SOP & Validation record | 3 | 2 | 1 | 6Low category & Risk Accepted | Adequate procedure no recommendation required. |  |  |  |  |

**Where: S=Severity; O=Occurrence Probability; D=Detection; Risk category 1-25 RPN is Low risk, 26-50 RPN is Medium Risk, 51-125 RPN is High Risk.**

|  |  |
| --- | --- |
| **Name of Facility/Equipment/Utility/System/Activity/Procedure/Unit Operation:** Entry & Exit with Common Change Rooms for Second Floor | Date:  |
| **S. No.** | **Recommended Action** | **Responsible Person** | **Target Date****of Completion** |
| 1. | NA | NA | NA |
| 2. | NA | NA | NA |

**CAPA:** Not required

**If required, mention CAPA No.:** NA

|  |  |  |
| --- | --- | --- |
| **Quality Risk Management Team** | **Reviewed By****Head Operations****Sign & Date** | **Approved By****Head QA****Sign & Date** |
| **Name** | **Department** | **Sign & Date** |
|  |  |  |
|  |  |  |
|  |  |  |
|  |  |  |

**QUALITY RISK ASSESSEMENT AND MITIGATION SUMMARY REPORT**

|  |
| --- |
| **Name of Equipment:** Entry & Exit With Common Change Rooms |

**Verification of Action Plan:** NA

**Remarks (if any):** The entire above failure mode and their Severity, Occurrence, Detection rating done and RPN No. is found between 03 to 09. Hence Risk is detected as low which is acceptable.

|  |  |
| --- | --- |
| **Verified By** **QA****Sign & Date** |  **Approved By**  **Head QA** **Sign & Date** |